North Utilities - OEM Service Criteria Excerpt

Applies to CWP-3 condenser-water pump train, CT-2 tower cell, and associated seal-flush and strainer components. Document reference: OEM-CWP3-NU-REV4.

# 1. Source priority and measurement rules

| source_id | rule | criteria text |
| --- | --- | --- |
| OEM-001 | technical thresholds | OEM limits control mechanical acceptance when they conflict with general site tolerance sheets. |
| OEM-002 | pump curve comparison | Pump readings must be compared at the same VFD speed or normalized by affinity laws. |
| OEM-003 | field readings | Do not use scaled BAS flow values unless the loop scale matches the transmitter scale or the value has been corrected. |
| OEM-004 | missing data | Do not backfill strainer DP, seal-flush pressure, or bearing defect frequency where readings were not collected. |

# 2. Pump performance and hydraulic criteria

| source_id | criterion | limit or rule | action |
| --- | --- | --- | --- |
| OEM-010 | TDH calculation | TDH ft = (discharge psi - suction psi) * 2.31 + elevation correction | Use verified suction and discharge pressure. |
| OEM-011 | flow curve deviation | Measured normalized head more than 10 ft below curve is below curve | Check scaling and suction restriction before pump wear conclusion. |
| OEM-012 | affinity laws | Q scales with speed ratio; head scales with speed ratio squared | Use for VFD speed normalization. |
| OEM-013 | flow transmitter scaling | BAS scale must match loop card before use as controlling flow | Use ultrasonic meter where BAS scale mismatch exists. |

# 3. Vibration, bearing temperature, and alignment

| source_id | component | alert | alarm or stop | interpretation |
| --- | --- | --- | --- | --- |
| OEM-020 | pump bearing vibration | 4.5 mm/s RMS | 7.1 mm/s RMS | Dominant 1x with elevated axial indicates alignment, soft foot, pipe strain, or coupling load unless defect frequencies are present. |
| OEM-021 | pump bearing temperature | 80 deg C review | 90 deg C stop and inspect | Do not claim bearing replacement unless inspection or parts issue is recorded. |
| OEM-022 | CWP-3 alignment offset | not applicable | 0.06 mm cold parallel offset | Applies to CWP-3, M-CWP-3, and CPL-CWP-3 train. |
| OEM-023 | CWP-3 alignment angular | not applicable | 0.05 mm per 100 mm cold angular | OEM tolerance overrides general site tolerance. |

# 4. Seal, flush, and strainer criteria

| source_id | criterion | normal range | warning or action |
| --- | --- | --- | --- |
| OEM-030 | mechanical seal leakage | dry or occasional film at start-up | visible mist, repeated wetting, or drip requires seal/flush investigation |
| OEM-031 | seal replacement verification | correct kit issue plus leak test record | reservation, wrong kit, or reversed transaction is not proof of installation |
| OEM-032 | seal-flush pressure | minimum 25 psi while pump runs at 47 to 50 Hz | below 25 psi with leakage is inadequate; missing pressure is unresolved |
| OEM-033 | strainer differential pressure | clean below 2 psi | monitor at 2 to 5 psi; action above 5 psi |

# 5. Cooling tower and bypass criteria

| source_id | criterion | limit | interpretation |
| --- | --- | --- | --- |
| OEM-040 | CT-2 approach | normal below 8 deg F at observed load | approach above 10 deg F can contribute to condenser-water temperature alarms |
| OEM-041 | fan gearbox vibration | alarm above 5.0 mm/s RMS | normal gearbox vibration does not explain CWP-3 bearing temperature |
| OEM-042 | basin screen condition | clean to light debris | matted screen can contribute to debris loading and strainer fouling |
| OEM-043 | bypass valve evidence | trend position is diagnostic only without stroke verification | do not call valve rebuilt unless kit issue and stroke check exist |

# 6. Required reconciliation cautions

A close-out note is not controlling when contradicted by inventory transactions, calibrated route readings, or OEM criteria. A replaced coupling spider does not close alignment. A tower approach excursion can explain temperature approach and chiller load sensitivity, but it does not explain pump 1x vibration or mechanical seal leakage without separate pump evidence.

# 7. Source ID index

| source_id range | content |
| --- | --- |
| OEM-001 to OEM-004 | Source priority and missing-data rules. |
| OEM-010 to OEM-013 | Pump performance and curve comparison criteria. |
| OEM-020 to OEM-023 | Vibration, bearing temperature, and alignment criteria. |
| OEM-030 to OEM-033 | Seal, flush, and strainer criteria. |
| OEM-040 to OEM-043 | Cooling tower and bypass criteria. |