North Utilities - CWP-3 Alignment and Baseplate Report

Evidence window: 2026-05-04 to 2026-05-18

Report ID: ALIGN-CWP3-2026-05-11 | Laser kit: ShaftLine SL-320 | Calibration due: 2026-09-30

# 1. Scope and asset identity

The alignment activity covered the CWP-3 pump, M-CWP-3 motor, and CPL-CWP-3 jaw coupling. CMMS work order WO-78164 recorded the asset as MCWP-3, but the machine train scope included the pump, motor, and coupling. The pump was held as the fixed machine. Coupling spacer length was 96 mm.

| source_id | item | recorded value | control note |
| --- | --- | --- | --- |
| ALIGN-001 | work order reference | WO-78164 | CMMS asset tag MCWP-3; corrected train scope is CWP-3, M-CWP-3, CPL-CWP-3. |
| ALIGN-002 | pump status | fixed machine | No pump foot movement recorded. |
| ALIGN-003 | motor status | movable machine | Horizontal and vertical moves applied at motor feet. |
| ALIGN-004 | coupling type | jaw coupling with elastomer spider | Spider replaced under WO-78125 but alignment not verified at that time. |

# 2. Tolerance basis

The contractor close-out used the general site tolerance sheet. The OEM criteria excerpt gives stricter tolerances for this pump train and controls acceptance for the final reconciliation.

| source_id | standard | parallel offset limit | angular limit | use in report |
| --- | --- | --- | --- | --- |
| ALIGN-010 | general site tolerance sheet | 0.20 mm | 0.20 mm per 100 mm | Used by contractor to mark PASS. |
| ALIGN-011 | OEM CWP-3 criterion | 0.06 mm cold | 0.05 mm per 100 mm cold | Controls final acceptance. |

# 3. Soft-foot and baseplate observations

| source_id | check | finding | status |
| --- | --- | --- | --- |
| ALIGN-020 | motor front inboard foot | 0.10 mm feeler entry before shimming | borderline soft foot |
| ALIGN-021 | shim change | 0.05 mm shim added at motor front inboard foot | partial correction |
| ALIGN-022 | post-shim verification | No loosen-and-repeat record after horizontal move | unresolved |
| ALIGN-023 | baseplate grout | hairline crack at pump north plinth corner, 70 mm long | open observation |
| ALIGN-024 | hold-down bolts | torque checked at four motor feet | verified |

# 4. Laser alignment readings

| source_id | alignment stage | vertical offset mm | vertical angular mm/100 mm | horizontal offset mm | horizontal angular mm/100 mm | contractor status |
| --- | --- | --- | --- | --- | --- | --- |
| ALIGN-030 | initial | -0.18 | -0.13 | +0.28 | -0.19 | fail |
| ALIGN-031 | after vertical move | +0.04 | -0.03 | +0.25 | -0.17 | not final |
| ALIGN-032 | after horizontal move | +0.04 | -0.03 | +0.11 | -0.08 | pass using site tolerance |
| ALIGN-033 | final recorded reading | +0.04 | -0.03 | +0.11 | -0.08 | pass using site tolerance |

OEM comparison: vertical readings are within OEM limits, but the final horizontal offset of +0.11 mm exceeds the 0.06 mm OEM offset limit and the final horizontal angular value of -0.08 mm per 100 mm exceeds the 0.05 mm per 100 mm OEM angular limit. The site PASS does not control the final technical status.

# 5. Pipe strain and final condition

| source_id | check | finding | reconciliation note |
| --- | --- | --- | --- |
| ALIGN-040 | suction spool loosened | horizontal offset changed by +0.07 mm when spool bolts were loosened | pipe strain likely present |
| ALIGN-041 | suction support clamp | clamp tightened after final laser reading | final reading may not represent post-clamp condition |
| ALIGN-042 | repeat laser after clamp | no repeat reading recorded | unresolved data gap |
| ALIGN-043 | run test | 1x vibration remained above alarm after alignment work | alignment issue not closed |

# 6. Technician summary

The work order pass label is not sufficient to close alignment. The report contains a pass/fail conflict: the machine train passes the general site tolerance but fails the OEM tolerance in the horizontal plane. A repeat alignment reading is missing after the suction support clamp was tightened. The coupling spider replacement is verified separately and does not close the alignment fault.

# 7. Source ID index

| source_id range | content |
| --- | --- |
| ALIGN-001 to ALIGN-004 | Scope, asset identity, and coupling description. |
| ALIGN-010 to ALIGN-011 | Tolerance basis and source of pass/fail conflict. |
| ALIGN-020 to ALIGN-024 | Soft-foot and baseplate observations. |
| ALIGN-030 to ALIGN-033 | Laser alignment readings. |
| ALIGN-040 to ALIGN-043 | Pipe-strain and unresolved repeat-reading evidence. |